## Sheet
Respondent ID | Collector ID | Start Date | End Date | IP Address | Email Address | First Name | Last Name | Custom Data 1 | Which Company Do You Represent? | [23 empty] | Please Provide Your Contact Information | [9 empty] | If needed, can the issuing company contact you directly to discuss your responses further? |  | Please see the Business Driver for this survey that describes our Load Analysis process/solution. Please provide a narrative description of your process and solution(s). Issuing Company's Response For 4-12kV planning, Ameren uses an in house developed program called Load Analysis. Load analysis holds all normal and emergency ratings for every substation transformer and feeder. After each summer or winter season, the peak temperature day is identified and the loading data for all feeders and substation is pulled out of our SCADA historian for that day. That data is then pushed into Load Analysis. The Engineer inputs the expected load growth, DER penetration, future projects, and other diversions on each feeder and substation into Load Analysis. A report is then generated that shows every feeder and substation load projection for the next 5 years.The distribution load projections are then summed up to the sub-transmission level (34-69kV) and put into PSS/E. The engineer runs PSS/E power flow analysis and manually inputs the resulting load projections for the next 5 years onto an excel spreadsheet. | What software do you use for 4-12KV and/or 34-69kV load forecasting and does it allow for scenarios (analyzing multiple future states with different assumptions on external factors ex: high eV with low DER or low eV with low DER)? Issuing Company's Response Ameren uses our in-house developed software, Load Analysis, for 4-12kV planning. For 34-69kV planning we pull data from PSS/E onto excel spreadsheets to identify overloads and resulting projects. Our planning process does not currently include multiple scenarios. | If your utility is considering or currently performing integrated system planning across generation, distribution, and transmission, what software are you considering or using? Issuing Company's Response We have just started to investigate integrated system planning and are identifying potential benefits to the business. We are in the early stages of identifying the existing processes and software that the planning groups use to see how they'd need to be integrated. | Please Select A Decline Reason Below If You Are Unable To Respond To This Survey. If You Have No Objections To This Survey, Please Skip This Section And Select "Done" At The Bottom Of This Page.
[9 empty] | AEP | Ameren | Arizona Public Service | Berkshire Hathaway Energy | CenterPoint Energy | Con Edison | Consumers Energy | Dominion | DTE Energy | Duke Energy | Duquesne Light | Entergy | Eversource | Exelon | NextEra Energy | NiSource | PG&E | PSEG | Sempra | Southern California Edison | Southern Company | Tampa Electric | Tennessee Valley Authority | Xcel Energy | Name | Company | Address | Address 2 | City/Town | State/Province | ZIP/Postal Code | Country | Email Address | Phone Number | Yes | No | Open-Ended Response | Open-Ended Response | Open-Ended Response | Company Does Not Pursue This Line of Business | Company Does Not Use This Application or Process | Determined To Be a Security Concern | Determined To Be Proprietary Information | Not A Function of I.T. In This Organization
118644380216 | 456830281 | 2024-07-09 19:42 | 2024-07-09 19:43 | 208.127.82.33 | [22 empty] | Sempra | [5 empty] | Sempra Unite Team | [7 empty] | uniteteam@sempra.com | 6196765926 | Yes | [5 empty] | Company Does Not Use This Application or Process
118644256947 | 456830281 | 2024-07-09 16:33 | 2024-07-09 16:37 | 137.91.114.225 | [6 empty] | Arizona Public Service | [21 empty] | Kevin Trujillo | [7 empty] | kevin.trujillo@aps.com | 480-476-4365 | Yes |  | On the distribution side of the business we use this very same process as listed above. We utilize cyme, Pi Vision and ADMS for all of our loading. | We utilize ADMS and Cyme and PI Vision. | None at this time
118644224125 | 456830281 | 2024-07-09 15:33 | 2024-07-09 16:12 | 216.99.180.122 | [17 empty] | Exelon | [10 empty] | Alfred Manzoni | [7 empty] | alfred.manzoni@exeloncorp.com | 667-313-2401 |  | No | PECO Distribution (4 kV, 13 kV, 34 kV) Capacity Planning maintains load forecasts for all distribution components (circuits, transformers, substations). Summer and winter load validation is completed by manually reviewing SCADA readings against the prior year’s forecast. Anticipated transfers and new business loads are added manually. An in-house developed Oracle-based tool with an API to assist planners with reviewing load data. Load estimates are completed with Cyme Dist software. PSS/E is used when needed for our 34 kV network system. | Tools mentioned above are currently used, but PECO along with the other Exelon operating companies are currently working on converging on a common tool to replace our current in-house planning tool to allow for scenario forecasting and planning DER. Cyme Dist will continue to be used for load estimating when needed. | In house Oracle based tool, PSS/E, and Cymdist
118644108362 | 456830281 | 2024-07-09 13:49 | 2024-07-09 13:57 | 198.8.7.71 | [15 empty] | Entergy | [12 empty] | Matt Dilback | [7 empty] | wdilbac@entergy.com | 601-941-5376 | Yes | [8 empty] | Not A Function of I.T. In This Organization
118644049351 | 456830281 | 2024-07-09 12:42 | 2024-07-09 12:45 | 158.106.52.10 | [11 empty] | Dominion | [16 empty] | Ephraim C Edmunds | [7 empty] | ephraim.c.edmunds@dominionenergy.com | 8043870805 | Yes |  | For distribution planning (< 69kV) Dominion Energy Virginia (DEV) uses an in house developed program called Distribution Model Interface (DMI). DMI s holds all normal and emergency ratings for every substation transformer and feeder. After each summer or winter season, the peak temperature day is identified and the loading data for all feeders and substation is pulled out of our SCADA historian for that day. That data is then pushed into DMI. The Engineer inputs the expected load growth, DER penetration, future projects, and other diversions on each feeder and substation into DMI. A report is then generated that shows every feeder and substation load projection for the next 10 years. | Dominion Energy Virginia (DEV) currently uses in-house developed software, DMI. We are currently in deployment of a commercially available forecasting platform that will provide for scenarios of various forecasts (i.e. EVs, building electrification, DER) | We have just started to investigate integrated system planning and are identifying potential benefits to the business. We are in the early stages of identifying the existing processes and software that the planning groups use to see how they'd need to be integrated.
118643275724 | 456830281 | 2024-07-08 13:16 | 2024-07-09 12:21 | 167.239.221.101 |  |  |  |  | AEP | [23 empty] | Pugal Jenardhanan | [7 empty] | pnjenardhanan@aep.com | 2487597236 | Yes |  | For 4-34.5kV planning, AEP uses an in house developed program called DGP (Distribution Grid Planner). All of the normal and emergency ratings / limiting factors of the system for all distribution transformers and feeders are stored and maintained in the DGP system by the distribution planning teams. The planners review the load details at the end of each season / predetermined date during the year to populate DGP from various sources including DMS, SCADA, and manual data collections. This review process includes applying any growth factors, future project work, transfers, new load, etc that would impact the forecast. The forecast goes out 10 years into the future. | AEP uses our in-house developed software, DGP (Distribution Grid Planner) for 4-34.5kV planning. This tool includes a sandbox environment that can be used to create different scenarios called “What-If Forecast”. The planner can take the existing forecast and create different scenarios in this environment to see how the system will be impacted. It is not currently a required part of the planning process, and we are investigating how best to incorporate our economic forecasting teams EV and DER penetration forecasts into our forecasting tools directly. | AEP has started to develop an integrated planning process across business units that involves a maturity model framework for each planning function including a set of capabilities required over time. Due to the nature of the planning functions, currently there is no plan to use a single software. The goal is that the process and framework developed will serve as the platform for integrated planning even if multiple software packages are utilized.
118643950885 | 456830281 | 2024-07-09 10:46 | 2024-07-09 10:53 | 199.125.55.10 | [19 empty] | NiSource | [8 empty] | Tim Noonan | [7 empty] | tnoonan@nisource.com | 6148699498 | Yes |  | I do not work in our Distribution planning portfolio but did reach out to the team that supports our distribution applications. CYME/CYMDIST does have load flow analysis and is the main program NIPSCO(our electric operating company) uses for 12/4 kV analysis of any load. The software can do the forecasting and multiple scenarios. For 34 kV and up analysis PSSE is used. | at NiSource for our one electric distribution Operating company for 4-12kV we use CYME/CYMDIST and it can do forecasting for multiple scenarios. for 34-69kV we use PSEE. | We have no plans to consolidate planning software.
118643422481 | 456830281 | 2024-07-08 16:22 | 2024-07-08 16:24 | 136.226.107.86 | [14 empty] | Duquesne Light | [13 empty] | Wesley Terek | [7 empty] | wterek@duqlight.com | n//a | Yes |  | c. For 23 kV distribution circuit planning, DLC pulls the annual hourly loading information from our PI data historian and assesses the operation status at each hour and accounts for any load transfers between neighboring circuits. A peak load is obtained from every circuit which is then used in our annual 10-year forecast. The 10-year forecast is determined by using a combination of expected growth from PJM, specific DER projects, and customer-related load growth. d. For 23 kV subtransmission circuit planning, DLC follows a similar procedure as above, by pulling the annual loading information. No forecast is prepared, as historical loading on these circuits is typically flat, and any load growth is assessed at the time of the request. e. Circuit ratings are maintained in an excel “database”. Substation ratings are maintained in a separate excel spreadsheet. Both are utilized in the 10-year forecast to identify when facilities are approaching 90% and 100% of their operating rating. f. Outside of forecasting, DLC utilizes CYME for detailed distribution and subtransmission circuit modeling and analysis purposes. An integration between CYME and DLC’s GIS system was recently completed (called CYME Gateway). DLC is investigating ways to integrate CYME distribution and subtransmission models with our transmission models in PSS\E using Python scripts. | DLC does not presently use software tools for distribution load forecasting. All distribution forecasting is done using excel spreadsheets. We evaluate the normal operating condition of the distribution circuits. | DLC is interested in and investigating integrated Asset Investment Planning tools, load forecasting tools based on AMI data, and more advanced power T&D power flow analysis tools such as PSS Sincal.
118643057652 | 456830281 | 2024-07-08 09:14 | 2024-07-08 09:16 | 136.226.59.89 | [16 empty] | Eversource | [11 empty] | David Lague | [7 empty] | david.lague@eversource.com | 6032547565 | Yes | [8 empty] | Not A Function of I.T. In This Organization
118641663102 | 456830281 | 2024-07-05 08:44 | 2024-07-05 08:46 | 204.124.152.26 | [12 empty] | DTE Energy | [15 empty] | Douglas Sigler | [7 empty] | douglas.sigler@dteenergy.com | 3132357504 | Yes | [8 empty] | Not A Function of I.T. In This Organization
118641134156 | 456830281 | 2024-07-04 14:18 | 2024-07-04 14:20 | 131.89.195.3 | [20 empty] | PG&E | [7 empty] | Brad | [7 empty] | bradley.detjen@pge.com | 6507699334 | Yes |  | PG&E Distribution Planning follows a similar process. Forecasting is performed in LoadSEER (Integral Analytics). Historical smartmeter AMI data is used as the load basis, but compared to SCADA as a cross-check. Known load applications are applied, and then spatial growth (capped by the California Energy Commission's IEPR forecast) is added to create growth forecasts for each feeder. Each feeder's peak usage hour is identified as the "strategic hour" for analysis. Distribution Engineers then use CYME's web-based Forecast Integration Tool to perform load flow studies and identify abnormal conditions on each feeder. Finally, Distribution Engineers design mitigations to resolve all abnormal conditions. | PG&E uses LoadSEER for distribution forecasting (voltages < 35 kV). LoadSEER has some support for multiple scenarios. | PG&E’s Integrated Grid Planning team is overseeing an effort for cross-workstream long term project portfolio planning that identifies project bundling efficiencies and unifies project prioritization in a risk-based framework. IGP is using Copperleaf software for this effort.
118636888700 | 456830281 | 2024-06-28 15:32 | 2024-06-28 15:35 | 165.225.223.5 | [18 empty] | NextEra Energy | [9 empty] | Richard Lingenfelder | [7 empty] | richard.lingenfelder@fpl.com | 561-904-3507 |  | No | For 4-25kV planning, FPL uses an in developed tool called LEAF (Line Engineering Analytics and Forecasting) which stores the normal and emergency ratings for all distribution circuits to monitor and is used by the planning team to select the annual peak for each distribution circuit and substation transformer. This application is also used to store known pockets of projected load growth within the service territory and to develop a multi-year forecast for all circuits. All the information housed in LEAF is applied to our distribution feeder models built on DNV’s Synergi Electric application, where we run various analyses on the entire system for the next 5 years to identify areas where facilities are at or near capacity and require investment to resolve the capacity constraints. We have a separate process where the distribution forecast is summed up to the transmission level (46 kV+) to develop a proportional distribution of the projected load growth. The distribution loads provide a ratio to which the 10 year corporate forecast is applied and PSS/E model updated for transmission studies. | DNV’s Synergi Electric does provide the ability to model scenarios with varying DER and EV load forecast and other assumptions. FPL is in the process of exploring these capabilities to develop processes to include these factors into our capacity planning process. Similarly, there are also several loading scenarios used to evaluate transmission system against TPL-001.5 standards as well as other sensitivities across the system. | FPL’s Distribution Planning team sums the distribution load forecast up to the transmission level to provide the Transmission Planning team a 6 year projected proportional distribution of the forecasted load growth. There are no current plans to integrate planning across distribution, transmission and generation.
118634333022 | 456830281 | 2024-06-21 08:07 | 2024-06-25 16:10 | 192.234.122.28 | [13 empty] | Duke Energy | [14 empty] | Gregg Borachok | [7 empty] | gregg.borachok@duke-energy.com | 7046071932 | Yes |  | Duke Energy’s narrative description is very similar to Ameren’s, but we’re incorporating some features that improve integration between Generation, Transmission, and Distribution. These features, such as the forecasting and ADP, are described in the report linked below. In June 2023, Berkley Lab and NREL published a report for the South Carolina Office of Regulatory Staff that describes our integrated planning approach. A link to that report is provided below. https://eta-publications.lbl.gov/sites/default/files/gmlc_4.2.2_memo_20230628_final.pdf | Forecasting is addressed in Section 2.1 of the report linked above. | Data is the key to improving integration. Duke relies on an internally developed platform to share information across domains and jurisdictions. The internally developed platform allows us to implement improvements to address evolving business needs and data availability.
118634197058 | 456830281 | 2024-06-25 12:13 | 2024-06-25 14:19 | 158.57.150.68 | [9 empty] | Con Edison | [18 empty] | Trevor Hanson | [7 empty] | hansont@coned.com | 212-460-3500 | Yes |  | At Con Edison, the responsibility for planning different parts of the system (transmission, sub-transmission/area substations and distribution network and non-network) are undertaken by different departments using different evaluation tools. The annual system planning process begins with the issuance of the network level peak demand forecasts after the summer load experience. Metered peak load data adjusted for design weather along with several load modifiers (e.g. various DER technologies, Demand Response and Energy Efficiency) are included in the Forecasts. Capabilities of sub-transmission feeders and area substation are developed based on each station's contingency design and most limiting equipment. Forecasts are compared with station and feeder capabilities, projected overloads identified, and capital projects that provide cost-effective solutions to address future load growth in the forecast are developed and recommended. Load relief solutions may entail cooling existing transformers, installing additional transformers or capacitor banks, transfer of load from one station to another with capacity headroom or establishing new transmission and area substations. PSS/E power flow modeling is used to determine sub-transmission supply feeder capabilities, while a proprietary in-house calculation tool using equipment emergency thermal ratings and station load power factor is used to determine substation capabilities. The current planning cycle involved the inclusion of probabilistic risk assessment at the area station level that adjusted the need timeline of certain projects to mitigate system risk | Con Ed has recently utilized three different load forecast scenarios to evaluate where sub-transmission and substation assets exceed their design capabilities and how timing of load relief projects are impacted. These loading sensitivities (which have differing assumptions around some forecast load modifiers, like EV proliferation) are inputted into PSS/E at the area station level to determine sub-transmission feeder deficiencies. These sensitivities are also compared to existing area station design capabilities to determine timing adjustments of system reinforcement projects, however the 'Base' forecast scenario is still used for capital planning by the Company. | I'm not sure on this. Certainly, there have been internal discussions around more integrated system planning and aligning on diverse range of objectives. However, my take is that the software tools currently being utilized by our engineering teams appear to be quite adequate to execute efficient and effective system planning for the near term.
118634207526 | 456830281 | 2024-06-25 12:28 | 2024-06-25 12:29 | 163.116.140.94 | [23 empty] | Southern California Edison |  |  |  |  | Erica J. Belleza | [7 empty] | Erica.Belleza@sce.com | 6265436182 |  | No | [7 empty] | Not A Function of I.T. In This Organization
118632197541 | 456830281 | 2024-06-21 18:57 | 2024-06-21 18:57 | 131.219.9.1 | [7 empty] | Berkshire Hathaway Energy | [20 empty] | Brandon Duncan | [7 empty] | brandon.duncan@midamerican.com | 5633338629 | Yes | [8 empty] | Not A Function of I.T. In This Organization
118632081149 | 456830281 | 2024-06-21 15:25 | 2024-06-21 16:06 | 208.87.237.201 | [27 empty] | Xcel Energy | Hassan Nadeem | [7 empty] | hassan.nadeem@xcelenergy.com | 6123225489 |  | No | Our process is very similar to yours, however, we collect non-coincident peak demands for each feeder, whereas what you describe is gathering feeder peaks coincident with the system peak. We use LoadSeer tool to manage this. | LoadSeer. | We are performing integrated system planning and have restructured our planning organizations to complete this. Our Modeling and Analytics team within ISP is actively reviewing the different modeling and forecasting software used for each commodity planning process and are considering opportunities for integrating these platforms.
118631059760 | 456830281 | 2024-06-20 09:19 | 2024-06-20 09:57 | 146.126.51.51 | [24 empty] | Southern Company |  |  |  | Christy Hyche & Philip Waters | [7 empty] | cghyche@southernco plwaters@southernco.com | 205-257-4116 205-257-4216 | Yes |  | We presently use Cyme software for all of our 46 kv and below sub-transmission and distribution planning processes. Additionally, we use the software for secondary grid and spot grid analysis. Our process is similar to what you described above for the 46 kV analysis. We use a feeder analysis and transpose the feeder peaks to a spreadsheet for totalized substation loading. The software performs load allocations based either on connected kva or kwH consumption. The feeder information is pulled from our GIS system yearly. DER information is manually placed on the feeders. | We presently use Cyme software for all of our 46 kv and below sub-transmission and distribution planning analysis. Additionally, we use the software for secondary grid and spot grid analysis. Our process is similar to what you described above. The 34.5 kV and below distribution systems use unbalanced analysis whereas the 46 kv uses balanced analysis. Masked loading caused by DER's is accounted for in our substation spreadsheets. | To my knowledge we aren't using an integrated analysis yet.
118630226742 | 456830281 | 2024-06-19 07:22 | 2024-06-19 07:48 | 12.171.196.205 | [25 empty] | Tampa Electric |  |  | Kristy Baksh | [7 empty] | kbaksh@tecoenergy.com | 8136351453 | Yes |  | TEC's distribution voltage is 13.2 kV and our sub-transmission voltage is 69kV. TEC uses 34.5kV to support the solar interconnections within our service area. In the past (through 2022), TEC utilized a similar method to Ameren for performing the distribution planning analysis, once the peak day was identified, TEC would pull the data from HIS into an excel spreadsheet for all feeders and substations. Any anomalies would be rectified (such as abnormal switching configurations, planned outages where load was transferred to adjacent substations) through a data intensive process internally known as Load Reconciliation. This process would take 6-8 weeks and involved the use of excel, reviewing past switching orders and conversations with system operators. Once complete, TEC would assume a distribution growth factor for years 2-10 and utilize excel to identify future loadings on feeders and substation transformers. The load data for future years would be provided to the transmission planner for input into PSS/E and utilized for the near-term transmission planning analysis - this is currently the only connection between Distribution Planning and Transmission Planning (utilizing load data based on actual peak conditions with a growth factor included for future years). When solutions are needed on the distribution system, TEC would have utilized both the excel spreadsheet and the Synergi Software. In 2022, TEC performed an upgrade on the Synergi software to include the Model Forge Solution, this allows TEC to utilize AMI data and has reduced the 6-8 week load reconciliation process to 1-2 days. TEC now utilizes Synergi's Multi-Model feature to create multiple cases showing various sensitivities with EVs, DERs and traditional load growth to model system peak with EV/DER, system peak without EV,DERs and we can now save these 'models' and utilize these Synergi models (in addition) to our excel based spreadsheets to perform our distribution planning analysis. TEC has written a white-paper on the Synergi Model Forge solution describing the ways it has changed our planning process and would be open to sharing both the white paper and an updated description of our planning process if Ameren would like to reach out to us. | TEC utilizes Synergi which includes a global irradiance curve for DERs. However, TEC can also manipulate the data in Synergi to impact DER output for any sensitivities that are required and can also update load data to include sensitivities related to EV load impacts. Within the last 2-years, TEC has been able to include multiple scenarios due to the benefits of the Synergi Multi-Model feature. | TEC has a nascent program on integrated system planning that lends itself to more synergies between Transmission Planning and Resource Planning. TEC has joined industry groups to continue to develop and enhance our Integrated System Planning process and form closer ties amongst all 3-departments (Resource, Transmission and Distribution). Currently each group utilizes their own individual software for their analyses and meet quarterly to update sensitivities for future studies.
118629429463 | 456830281 | 2024-06-18 08:58 | 2024-06-18 09:01 | 68.54.53.3 | [26 empty] | Tennessee Valley Authority |  | Jack Flack | [7 empty] | jeflack@tva.gov | 423-751-4537 | Yes |  |  |  |  | Company Does Not Pursue This Line of Business
118629018078 | 456830281 | 2024-06-17 17:33 | 2024-06-17 17:33 | 146.126.51.51 | [5 empty] | Ameren | [22 empty] | Charlie Schaeffer | [7 empty] | cschaeffer@ameren.com | 3148613259 | Yes |  | For 4-12kV planning, Ameren uses an in house developed program called Load Analysis. Load analysis holds all normal and emergency ratings for every substation transformer and feeder. After each summer or winter season, the peak temperature day is identified and the loading data for all feeders and substation is pulled out of our SCADA historian for that day. That data is then pushed into Load Analysis. The Engineer inputs the expected load growth, DER penetration, future projects, and other diversions on each feeder and substation into Load Analysis. A report is then generated that shows every feeder and substation load projection for the next 5 years. The distribution load projections are then summed up to the sub-transmission level (34-69kV) and put into PSS/E. The engineer runs PSS/E power flow analysis and manually inputs the resulting load projections for the next 5 years onto an excel spreadsheet. | Ameren uses our in-house developed software, Load Analysis, for 4-12kV planning. For 34-69kV planning we pull data from PSS/E onto excel spreadsheets to identify overloads and resulting projects. Our planning process does not currently include multiple scenarios. | We have just started to investigate integrated system planning and are identifying potential benefits to the business. We are in the early stages of identifying the existing processes and software that the planning groups use to see how they'd need to be integrated.